## Table 1 A & B
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | ASTM E2618 |  | VERSION YEAR: |  | 2017 | LOCATION: | Middleton
RESULTS
PASS | X |  | FAIL |  |  | NO PASS/FAIL
Table 1A. Data Summary Part A
[6 empty] | Q | Wfuel | MCave | Qin | Qout
Category | Run No. | Load % Capacity | Target Load | Actual Load | Actual Load | Test Duration | Wood Weight as-fired | Wood Moisture | Heat Input | Heat Output
|  |  | Btu/hr | Btu/hr | % of Max | hrs | lb | % DB | Btu | Btu
I | 2 | <15% of Max | 25500 | 23857.9946 | 14.03% | 14.0167 | 86.41 | 22.5917 | 606179.6436 | 334409.5577
II | 3 | 16-24% of Max | 40800 | 39041.9216 | 22.97% | 9.75 | 76.71 | 22.665 | 537811.0074 | 380658.7352
III | 4 | 25-50% of max | 85000 | 74281.1449 | 43.69% | 5.1167 | 76.46 | 21.6998 | 540309.9958 | 380071.8579
IV | 1 | Max capacity | 170000 | 155802.0206 | 91.65% | 3.1333 | 79.8 | 22.5792 | 559866.3828 | 488179.6647
Table 1B. Data Summary Part B
|  |  | T2 Min | ET | E | E | Eg/hr | Eg/kg | hdel | hSLM
Category | Run No. | Load % Capacity | Min Return Water Temp. | Total PM Emissions | PM Output Based | PM Output Based | PM Rate | PM Factor | Delivered Efficiency | Stack Loss Efficiency
|  |  | ºF | g | lb/mmBtu Out | g/MJ | g/hr | g/kg | % | %
I |  | <15% of Max | 162.61 | 23.1817 | 0.15283 | 0.065707 | 1.6539 | 0.72486 | 55.17% | 36.77%
II |  | 16-24% of Max | 159.62 | 24.8108 | 0.14369 | 0.061781 | 2.5447 | 0.87442 | 70.78% | 73.16%
III |  | 25-50% of max | 157.15 | 18.8915 | 0.10958 | 0.047114 | 3.6922 | 0.66273 | 70.34% | 76.63%
IV |  | Max capacity | 132.48 | 15.2454 | 0.068849 | 0.029601 | 4.8656 | 0.51614 | 87.2% | 80.03%
* NOTE:

## Hang Tag Info
|  | CLIENT: |  | Alternate Heating Systems | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: | 2015 | LOCATION: | Middleton
RESULTS
PASS | X |  | FAIL |  | NO PASS/FAIL
Table 1C: Hang Tag Information
| MANUFACTURER: | Alternate Heating Systems
| MODEL NUMBER: | SE120
| 8-HOUR OUTPUT RATING: | Qout-8hr | 52361.2765 | Btu/hr
| 8-HOUR AVERAGE EFFICIENCY: | havg-8hr | 70.61% | (Using higher heating value)
| AVERAGE EFFICIENCY RATING: | havg | 70.87% | (Using higher heating value)
| PARTICULATE EMISSIONS: | Eavg | 3.1891 | GRAMS/HR (average)
| PARTICULATE EMISSIONS: | Eavg | 0.15283 | LBS/MILLION Btu OUTPUT Cat 1
| PARTICULATE EMISSIONS: | Eavg | 0.14369 | LBS/MILLION Btu OUTPUT Cat 2
| PARTICULATE EMISSIONS: | Eavg | 0.10958 | LBS/MILLION Btu OUTPUT Cat 3
| PARTICULATE EMISSIONS: | Eavg | 0.068849 | LBS/MILLION Btu OUTPUT Cat 4

## Averaged Data
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS |  |  | FAIL |  |  | NO PASS/FAIL |  | X
Table 2. Averaged Data
| Category | Run No. | Weighting Factor | hdel,i x Fi-HHV | Eg/hr x Fi | hsl,i x Fi-HHV | CO (g/min)
| I | 2 | 0.25 | 0.13792 | 0.41347 | 0.091914 | 0.9652
| II | 3 | 0.25 | 0.17695 | 0.63617 | 0.18289 | 1.0233
| III | 4 | 0.25 | 0.17586 | 0.92304 | 0.19157 | 1.2049
| IV | 1 | 0.25 | 0.21799 | 1.2164 | 0.20008 | 1.2951
| Totals |  | 1 | 70.87% | 3.1891 | 66.65% | 4.4885

## Data
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS | X |  | FAIL |  |  | NO PASS/FAIL
Data for Outdoor Wood Fired hydronic Heating Appliances
|  | CAT | Load % Capacity | Tgt Load (Btu/hr) | Act Load (Btu/hr) | Test Duration | WoodWt | Qin | Qout | hN | ET | E | E Output | E Input | E | E
[6 empty] | (Hours) | (Lb) | (Btu) | (Btu) | (%) | (g) | (g/MJ) | (lb/mmbtu) | (lb/mmbtu) | (g/hr) | (g/Kg)
|  | I | <15% of max | 25500 | 23857.9946 | 14.0167 | 86.41 | 606179.6436 | 334409.5577 | 55.17% | 23.1817 | 0.065707 | 0.15283 | 0.08431 | 1.6539 | 0.72486
|  | II | 16 – 24% of max | 40800 | 39041.9216 | 9.75 | 76.71 | 537811.0074 | 380658.7352 | 70.78% | 24.8108 | 0.061781 | 0.14369 | 0.10171 | 2.5447 | 0.87442
|  | III | 25 -50% of max | 85000 | 74281.1449 | 5.1167 | 76.46 | 540309.9958 | 380071.8579 | 70.34% | 18.8915 | 0.047114 | 0.10958 | 0.077083 | 3.6922 | 0.66273
|  | IV | Max capacity | 170000 | 155802.0206 | 3.1333 | 79.8 | 559866.3828 | 488179.6647 | 87.2% | 15.2454 | 0.029601 | 0.068849 | 0.060033 | 4.8656 | 0.51614
Efficiency
|  |  | Average BTU/hr for 8 hr burn time |  | 52361.2765 | 70.61% |  | Y1 | 9.75 | Test duration above 8 hours
[6 empty] | HHV |  | Y2 | 5.12 | Test duration just below 8 hours
[8 empty] | X1 | 39042 | Actual load (BTU/hr) for duration Y1
[5 empty] | If the test is ASTM put a 0, if EPA put a 1 | 0 |  | X2 | 74281 | Actual load (BTU/hr) for duration Y2
[8 empty] | Z1 | 70.8% | Efficiency for duration Y1 HHV
|  |  | Maximum output rating BTU/hr: | 170000 |  |  |  | Z2 | 70.3% | Efficiency for duration Y2 HHV
Average Efficiency
Weighting
|  | Category | Factor | h x Fi,HHV
|  | I | 0.25 | 0.13792
|  | II | 0.25 | 0.17695
|  | III | 0.25 | 0.17586
|  | IV | 0.25 | 0.21799
|  | Totals | 1 | 0.70871
Year Round Use Weighting
|  |  | Weighting |  |  |  | Input | Output
|  | Category | Factor | h x Fi, HHV | Eg/MJ,I x Fi | Eg/kg,I x F i | Elb/mmbtu x Fi | Elb/mmbtu x Fi | Eg/hr x Fi
|  | I | 0.437 | 0.24108 | 0.028714 | 0.31676 | 0.036844 | 0.066786 | 0.72274
|  | II | 0.238 | 0.16845 | 0.014704 | 0.20811 | 0.024206 | 0.034199 | 0.60564
|  | III | 0.275 | 0.19344 | 0.012956 | 0.18225 | 0.021198 | 0.030135 | 1.0153
|  | IV | 0.05 | 0.043598 | 0.0014801 | 0.025807 | 0.0030017 | 0.0034424 | 0.24328
|  | Totals | 1 | 0.64658 | 0.057854 | 0.73293 | 0.085249 | 0.13456 | 2.587
'file:///tmp/in/input.xls'#$Data
Remember to use Paste special when copying to this area, values only!
|  | Category 1 test results Paste in F51 | [5 empty] | Category 2 test results paste in L51
|  |  |  | Run Number | 2 |  |  |  |  | Run Number | 3
|  |  |  | Test Date | 2021-09-22 |  |  |  |  | Test Date | 2021-09-23
|  |  |  | Total Test Fuel Weight (lb) | 86.41 |  |  |  |  | Total Test Fuel Weight (lb) | 76.71
|  |  |  | Avg. Test Fuel Moisture (% dry) | 22.5917 |  |  |  |  | Avg. Test Fuel Moisture (% dry) | 22.665
|  |  |  | Avg. Temp. of Water in load side (o F) | 117.3411 |  |  |  |  | Avg. Temp. of Water in load side (o F) | 113.4639
|  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 94.6453 |  |  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 89.8737
|  |  |  | Liquid Flow Rate (gal/min) | 0.50991 |  |  |  |  | Liquid Flow Rate (gal/min) | 0.84558
|  |  |  | Test Duration (min) | 841 |  |  |  |  | Test Duration (min) | 585
|  |  |  | Burn Rate (kg/hr) | 2.281 |  |  |  |  | Burn Rate (kg/hr) | 2.9094
|  |  |  | Emissions (g) | 23.1817 |  |  |  |  | Emissions (g) | 24.8108
|  |  |  | Beginning Dry Gas Meter Reading (ft3) | 0 | 0 |  |  |  | Beginning Dry Gas Meter Reading (ft3) | 0 | 0
|  |  |  | Final Dry Gas Meter Reading (ft3) | 119.2422 | 119.2979 |  |  |  | Final Dry Gas Meter Reading (ft3) | 82.8417 | 82.8336
|  |  |  | Average Barometric Pressure (“Hg) | 29.225 |  |  |  |  | Average Barometric Pressure (“Hg) | 29.035
|  |  |  | Average Delta p (inches of water) | 0.12902 |  |  |  |  | Average Delta p (inches of water) | 0.12988
|  |  |  | Average Delta H (inches of water) | 0 |  |  |  |  | Average Delta H (inches of water) | 0
|  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 21.7744 |  |  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 21.8916
|  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 1026.0973 |  |  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 1031.6209
|  |  |  | Water Density | 8.3226 |  |  |  |  | Water Density | 8.325
|  |  |  | Water Specific Heat | 1.0012 | MU |  |  |  | Water Specific Heat | 1.0012 | MU
|  |  |  | Total Output | 334409.5577 | 3795.6491 |  |  |  | Total Output | 380658.7352 | 4306.2689
|  |  |  | Emissions g/MJ | 0.065707 |  |  |  |  | Emissions g/MJ | 0.061781
|  |  |  | Emissions lb/MMBtu Input | 0.08431 |  |  |  |  | Emissions lb/MMBtu Input | 0.10171
|  |  |  | Emissions lb/MMBtu Output | 0.15283 | 0.0081076 |  |  |  | Emissions lb/MMBtu Output | 0.14369 | 0.0073952
|  |  |  | Efficiency | 0.55167 | 1.0942 |  |  |  | Efficiency | 0.70779 | 1.3878
|  |  |  | g/kg | 0.72486 |  |  |  |  | g/kg | 0.87442
|  |  |  | Input | 606179.6436 |  |  |  |  | Input | 537811.0074
|  | Category 3 test results paste in F81 | [5 empty] | Category 4 test results Paste in L81
|  |  |  | Run Number | 4 |  |  |  |  | Run Number | 1
|  |  |  | Test Date | 2021-09-24 |  |  |  |  | Test Date | 2021-09-21
|  |  |  | Total Test Fuel Weight (lb) | 76.46 |  |  |  |  | Total Test Fuel Weight (lb) | 79.8
|  |  |  | Avg. Test Fuel Moisture (% dry) | 21.6998 |  |  |  |  | Avg. Test Fuel Moisture (% dry) | 22.5792
|  |  |  | Avg. Temp. of Water in load side (o F) | 95.6314 |  |  |  |  | Avg. Temp. of Water in load side (o F) | 78.8583
|  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 73.0949 |  |  |  |  | Temp. Diff. in/out of Heat Exchanger (o F) | 32.8591
|  |  |  | Liquid Flow Rate (gal/min) | 2.0788 |  |  |  |  | Liquid Flow Rate (gal/min) | 9.9013
|  |  |  | Test Duration (min) | 307 |  |  |  |  | Test Duration (min) | 188
|  |  |  | Burn Rate (kg/hr) | 5.5696 |  |  |  |  | Burn Rate (kg/hr) | 9.4243
|  |  |  | Emissions (g) | 18.8915 |  |  |  |  | Emissions (g) | 15.2454
|  |  |  | Beginning Dry Gas Meter Reading (ft3) | 0 | 0 |  |  |  | Beginning Dry Gas Meter Reading (ft3) | 0 | 0
|  |  |  | Final Dry Gas Meter Reading (ft3) | 43.5516 | 43.5408 |  |  |  | Final Dry Gas Meter Reading (ft3) | 26.6213 | 26.6121
|  |  |  | Average Barometric Pressure (“Hg) | 28.87 |  |  |  |  | Average Barometric Pressure (“Hg) | 29.135
|  |  |  | Average Delta p (inches of water) | 0.12598 |  |  |  |  | Average Delta p (inches of water) | 0.12047
|  |  |  | Average Delta H (inches of water) | 0 |  |  |  |  | Average Delta H (inches of water) | 0
|  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 21.4384 |  |  |  |  | Average Gas Velocity in Tunnel (feet/sec) | 20.7717
|  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 1010.2643 |  |  |  |  | Average Gas Flow Rate in Dilution Tunnel (Qsd) (dscfm) | 978.8478
|  |  |  | Water Density | 8.3324 |  |  |  |  | Water Density | 8.3322
|  |  |  | Water Specific Heat | 1.0012 | MU |  |  |  | Water Specific Heat | 1.0012 | MU
|  |  |  | Total Output | 380071.8579 | 4905.7886 |  |  |  | Total Output | 488179.6647 | 9556.6028
|  |  |  | Emissions g/MJ | 0.047114 |  |  |  |  | Emissions g/MJ | 0.029601
|  |  |  | Emissions lb/MMBtu Input | 0.077083 |  |  |  |  | Emissions lb/MMBtu Input | 0.060033
|  |  |  | Emissions lb/MMBtu Output | 0.10958 | 0.0065665 |  |  |  | Emissions lb/MMBtu Output | 0.068849 | 0.0050497
|  |  |  | Efficiency | 0.70343 | 1.5013 |  |  |  | Efficiency | 0.87196 | 2.2319
|  |  |  | g/kg | 0.66273 |  |  |  |  | g/kg | 0.51614
|  |  |  | Input | 540309.9958 |  |  |  |  | Input | 559866.3828

## B415 Cat 1
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS |  |  | FAIL |  |  | NO PASS/FAIL |  | X
|  | HHV Basis | LHV Basis
| Overall Efficiency | 36.77% | 39.6%
| Combustion Efficiency | 92.44% | 92.44%
| Heat Transfer Efficiency | 39.77% | 42.84%
| Output Rate (kJ/h) | 16394.0459 | 15551.5231 | (Btu/h)
| Burn Rate (kg/h) | 2.2422 | 4.9418 | (lb/h)
| Input (kJ/h) | 44590.6875 | 42299.0829 | (Btu/h)
| Test Load Weight (dry kg) | 31.4282 | 69.2678 | dry lb
| MC wet (%) | 18.43
| MC dry (%) | 22.5941
| Particulate (g ) | 23.18
| CO (g) | 3246.9207
| Test Duration (h) | 14.0167
| Emissions | Particulate | CO
| g/MJ Output | 0.10087 | 14.13
| g/kg Dry Fuel | 0.50219
| g/h | 1.6537 | 231.6471 | 3.8608 | g/min
| lb/MM Btu Output | 0.23444 | 32.839

## B415 Cat 2
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS |  |  | FAIL |  |  | NO PASS/FAIL |  | X
|  | HHV Basis | LHV Basis
| Overall Efficiency | 73.16% | 78.79%
| Combustion Efficiency | 93.77% | 93.77%
| Heat Transfer Efficiency | 78.02% | 84.03%
| Output Rate (kJ/h) | 42337.0293 | 40161.2447 | (Btu/h)
| Burn Rate (kg/h) | 2.91 | 6.4137 | (lb/h)
| Input (kJ/h) | 57872.0973 | 54897.9345 | (Btu/h)
| Test Load Weight (dry kg) | 28.373 | 62.534 | dry lb
| MC wet (%) | 18.48
| MC dry (%) | 22.6693
| Particulate (g ) | 24.81
| CO (g) | 2394.6313
| Test Duration (h) | 9.75
| Emissions | Particulate | CO
| g/MJ Output | 0.060104 | 5.8011
| g/kg Dry Fuel | 0.5375
| g/h | 2.5446 | 245.6032 | 4.0934 | g/min
| lb/MM Btu Output | 0.13969 | 13.4823

## B415 Cat 3
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS |  |  | FAIL |  |  | NO PASS/FAIL |  | X
|  | HHV Basis | LHV Basis
| Overall Efficiency | 76.63% | 82.53%
| Combustion Efficiency | 97.36% | 97.36%
| Heat Transfer Efficiency | 78.71% | 84.77%
| Output Rate (kJ/h) | 84899.7609 | 80536.5924 | (Btu/h)
| Burn Rate (kg/h) | 5.5712 | 12.2789 | (lb/h)
| Input (kJ/h) | 110794.484 | 105100.5339 | (Btu/h)
| Test Load Weight (dry kg) | 28.506 | 62.8272 | dry lb
| MC wet (%) | 17.83
| MC dry (%) | 21.6989
| Particulate (g ) | 18.89
| CO (g) | 1479.5733
| Test Duration (h) | 5.1167
| Emissions | Particulate | CO
| g/MJ Output | 0.043485 | 3.406
| g/kg Dry Fuel | 0.40924
| g/h | 3.6919 | 289.1674 | 4.8195 | g/min
| lb/MM Btu Output | 0.10106 | 7.9158

## B415 Cat 4
|  | CLIENT: |  | Alternate Heating Systems |  | PERFORMED BY: |  | Ken Slater
|  | PROJECT #: |  | G104711998 |  | REVIEWED BY: |  | Brian Ziegler
|  | PRODUCT: |  | Outdoor Hydronic Heater |  | MODEL: |  | SE120
SAMPLE ID #: |  | MID2109200959-001 |  |  |  | DATE: |  | 2021-09-28
STANDARD(S): |  | EPA Method 28 WHH |  | VERSION YEAR: |  | 2015 | LOCATION: | Middleton
RESULTS
PASS |  |  | FAIL |  |  | NO PASS/FAIL |  | X
|  | HHV Basis | LHV Basis
| Overall Efficiency | 80.03% | 86.2%
| Combustion Efficiency | 97.9% | 97.9%
| Heat Transfer Efficiency | 81.75% | 88.05%
| Output Rate (kJ/h) | 150036.4279 | 142325.7558 | (Btu/h)
| Burn Rate (kg/h) | 9.4269 | 20.7769 | (lb/h)
| Input (kJ/h) | 187472.5458 | 177837.9567 | (Btu/h)
| Test Load Weight (dry kg) | 29.5376 | 65.1008 | dry lb
| MC wet (%) | 18.42
| MC dry (%) | 22.5791
| Particulate (g ) | 15.25
| CO (g) | 973.8895
| Test Duration (h) | 3.1333
| Emissions | Particulate | CO
| g/MJ Output | 0.032439 | 2.0716
| g/kg Dry Fuel | 0.33038
| g/h | 4.867 | 310.8158 | 5.1803 | g/min
| lb/MM Btu Output | 0.07539 | 4.8146